## 6_build+resid_11032020
LoadShapes built from https://www.energy.gov/eere/buildings/commercial-reference-buildings using the REopt site: https://reopt.nrel.gov/tool/ with .1 $/kWh and 20$/kW/month demand charge in 2017
Energy.gov reference Loadshpaes are not built for 24/7 operation, and have dips on weekends
*Assume average of 50% of target load across the whole year
Building to be modeled | Description | Ref building type | Area (ft^2) of reference building | Specified Geography | max kW load target (for modeling Laughlin) | Inputted Annual Consumption (kWh) into Reopt | Average Load (kW) from downloaded shape | Min Load (kW) from downloaded shape | Max Load (kW) from downloaded shape | Default Annual Consumption (kWh, as reported by REopt)
hangar_large_2_e.gov.csv | Large airplane hangar | Warehouse | 52000 | Miami, FL | 300 | 1314000 | 150 | 27.4 | 480 | 202082
hangar_medium_2_e.gov.csv | Medium Airplane hangar | Warehouse | 52000 | Atlanta, GA | 200 | 876000 | 100 | 16.57 | 351.89 | 223009
hospital_e.gov.csv | On-basehospital | Hospital | 241351 | Atlanta, GA | 1000 | 4380000 | 500 | 296 | 801 | 9054747
comms_data_2_e.gov.csv | Communications/office/data center | Medium Office | 53628 | Miami, FL | 600 | 2628000 | 300 | 52.24 | 757.76 | 1021224
terminal_2_e.gov.csv | Terminal building to hoouse recruits | Supermarket | 45000 | Miami, FL | 500 | 2190000 | 250 | 83.87 | 429.38 | 2260929
tower_e.gov.csv | Flight tower with radar, etc | Hotel Small | 5500 | Miami, FL | 400 | 1752000 | 200 | 85 | 351 | 972090
3MW_resid_e.gov.csv | Residential load | Midrise Apartment | 33740 | Miami, FL | 3000 | 13140000 | 1500 | 535 | 3364 | 424956
6_building_resid_combined_11032020.csv | Full installation load added together |  |  |  |  | 26280000 | 3000 | 1325.5 | 6264
Crit_loads_no_resid_11032020.csv | Critical loads without residual |  |  |  |  | 13140000 | 1500 | 772.3 | 2975
Scenario constants: | Miami, FL; outage; critical load factor 70%; 2017; 20,000 gallons of diesel (not all of which gets burned)
Scenario | LoadShape file | $/kWh | $/kw/month | Generation Mix: | Length of Outage (hr specified): | Start date of outage | Resilience results: | Res NPV ($) | Res Average outage survived (hr): | Res Prob surviving 168 hr outage (%) | Result:
BASE CASE: full load 1 week outage mid summer | 6_building_resid_combined_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 2,214 kW Diesel 8,002 kW PV 1,212 kW Battery 4,055 kWh Battery | 1645427 | 292 | 77 | BASE CASE: With unlimited fuel and 70% critical load, system is profitable
full load 1 day outage | 6_building_resid_combined_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 24 | 8/14/2017 8am | 2,181 kW Diesel 7,927 kW PV 1,208 kW Battery 4,010 kWh Battery | 2294249 | 281 | 74 | At 24 hour outage with same as base case, system stays largely the same but is more profitable
full load 1 week outage mid winter | 6_building_resid_combined_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 1/16/2017 8am | 1,792 kW Diesel 7,668 kW PV 1,112 kW Battery 3,223 kWh Battery | 2180251 | 117 | 27 | Winter resiliency estimate greatly decreases estimate of week-long survivability
Critical (flight ready) loads | Crit_loads_no_resid_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 976 kW Diesel 4,473 kW PV 673 kW Battery 1,961 kWh Battery | 937421 | 393 | 71 | More cost effective (by $700,000) on the larger grid than separating critical and non critical loads, with fewer resources (200kw less genset and 500 kWh less battery) needed in the full mircogrid.
Residential (non-critical) loads | 3MW_resid_e.gov.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 1,387 kW Diesel 3,701 kW PV 660 kW Battery 2,580 kWh Battery | -12437 | 544 | 77 | Residential on it's own
Hospital islanded | hospital_egov.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 312 kW Diesel 1,273 kW PV 181 kW Battery 564 kWh Battery | 185930 | 316 | 58 | Largest individual load receives more average resiliency, but lower probably of lasting 1 week; is cost effective on it's own
Tower Islanded | tower_egov.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 142 kW Diesel 441 kW PV 95 kW Battery 371 kWh Battery | -25266 | 283 | 50 | Smallest individual load is not cost effective to island

## 6_buildings_10282020
33740 | 33.74 | 35 units
19
2009 seattle ecotope data from https://www.seattle.gov/Documents/Departments/OSE/MF-Billing-Analysis-MidRise2009.pdf
at ~70% energy from electricity
Units | kWh/yr | kWh/yr/unit
19 | 184036 | 9686.1053
49 | 297959 | 6080.7959
44 | 427938 | 9725.8636
mean |  | kWh/yr/unit |  |  |  | kWhr/day/unit
76 | 505713 | 6654.1184 |  |  |  | 18.2305
|  | 232894.1447 |  | Average annual consumtion kWh for a 35 unit building of 1000 square ft units in Seattle
LoadShapes built from https://www.energy.gov/eere/buildings/commercial-reference-buildings using the REopt site: https://reopt.nrel.gov/tool/ with .1 $/kWh and 20$/kW/month demand charge in 2017
Energy.gov reference Loadshpaes are not built for 24/7 operation, and have dips on weekends
*Assume average of 50% of target load across the whole year
Building to be modeled | Description | Ref building type | Area (ft^2) of reference building | Specified Geography |  | max kW load target (for modeling Laughlin) | Inputted Annual Consumption (kWh) into Reopt | Average Load (kW) from downloaded shape | Min Load (kW) from downloaded shape | Max Load (kW) from downloaded shape | Default Annual Consumption (kWh, as reported by REopt) |  | 10000
hangar_large_e.gov.csv | Large airplane hangar | Warehouse | 52000 | Miami, FL |  | 1000 | 4380000 | 500 | 91.5 | 1599 | 202082 | *refit with residential | 6
hangar_medium_e.gov.csv |  | Warehouse | 52000 | Atlanta, GA |  | 800 | 3504000 | 400 | 66.27 | 1408 | 223009 | *refit with residential
hospital_e.gov.csv | On-basehospital | Hospital | 241351 | Atlanta, GA |  | 1000 | 4380000 | 500 | 296 | 801 | 9054747
comms_data_e.gov.csv | Communications/office/data center | Medium Office | 53628 | Miami, FL |  | 1000 | 4380000 | 500 | 87 | 1263 | 1021224
terminal_e.gov.csv | Terminal building to hoouse recruits | Supermarket | 45000 | Miami, FL |  | 800 | 3504000 | 400 | 134 | 687 | 2260929
tower_e.gov.csv | Flight tower with radar, etc | Hotel Small | 5500 | Miami, FL |  | 400 | 1752000 | 200 | 85 | 351 | 972090
|  |  |  | Sum: |  | 5000 | 21900000 | 5000 | 1818.77 | 11944 | 13734081
6_building_combined_10282020.csv | Full installation load added together | [5 empty] | 21900002 | 2500 | 1059 | 5835
Analysis of full load 6_building_combined_10282020.csv as prepared by https://reopt.nrel.gov/tool/:
Scenario constants: | .10$/kWh, 10$/kw/month in Miami, FL; outage; critical load factor 70%; loadshape = 6_building_combined_10282020.csv in 2017
*Reopt assumes full battery charge when modeling outage
Generation Mix: | Length of Outage (hr specified): | Start date of outage | Resilience results: | Res NPV | Res Average outage survived: | Res Prob surviving specified outage | Financial results: | Fin NPV | Fin Average outage survived:
PV + Battery | 24 | Jul 25th 2am (peak season | 9,714 kW PV 2,036 kW Battery 13,137 kWh Battery | -1689564 | 8 |  | 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1
PV + Battery+ Wind | 24 | Jul 25th 2am (peak season | Wind not recommended, defaults to PV+Battery as above
PV + Battery + Diesel | 24 | Jul 25th 2am (peak season | 593 kW Diesel 8,653 kW PV 1,551 kW Battery 6,932 kWh Battery | -154734 | 14 |  | 0 kW Diesel 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1
PV + Battery | 168 | Jul 25th 2am (peak season | 11,924 kW PV 2,857 kW Battery 24,388 kWh Battery | -5944586 | 70 | 13% | 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1
PV + Battery+ Wind | 168 | Jul 25th 2am (peak season | 11,638 kW PV 2,810 kW Battery 24,338 kWh Battery 268 kWh Wind | -5920757 | 81 | 16% | 6,284 kW PV 140 kW Battery 185 kWh Battery 14 kWh Wind | 1931723 | 1
PV + Battery + Diesel | 168 | Jul 25th 2am (peak season | 1,666 kW Diesel 6,710 kW PV 368 kW Battery 562 kWh Battery | 357608 | 69 | 12% | 0 kW Diesel 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1 | *Added 15000 gallons of diesel available to get this to turn on
PV + Battery + Diesel | 168 | Feb 2 2am (offpeak season) | 1,920 kW Diesel 6,705 kW PV 731 kW Battery 1,449 kWh Battery | 67193 | 164 | 59%
PV + Battery + Diesel | 168 | July 3 4pm (annual peak auto selected) | 1,823 kW Diesel 6,857 kW PV 756 kW Battery 1,263 kWh Battery | 116395 | 158 | 55% |  |  |  | *Reopt assumes 13.16 kWh per gallon of diesel, which is a little low for a 1MW genset
PV + Battery | N/A on microgridDesign | [5 empty] | 0 kW Diesel 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1 | *not incorporating the resiliency outputs based on outages in microgridDesign, and the economic is not what we need