## 12282020_Lehigh
Lehigh.dss 4 microgrid system | [17 empty] | 240 | 168
480
Json converter: https://onlinejsontools.com/convert-json-to-text
Reopt API docs: https://developer.nrel.gov/docs/energy-optimization/reopt-v1/
[16 empty] | Scenario constants: | Miami, FL; outage; critical load factor 70%; 2017; 30,000 gallons of diesel (not all of which gets burned)
[10 empty] | *To build the demand_loads for each microgrid, I ran the full model in microgrid.py and pulled the loadshapes from loadShape.csv |  | 0.40181
[10 empty] | *Calculated using all loads connected to gen bus added together | [5 empty] | *Resilience optimization outputs |  |  |  | *without incentives | *I am not sure that the NPV includes capital cost? |  |  | *minimum survived outage is often 0 hours
Microgrid name | Loads in Lehigh.dss | Switch in Lehigh.dss | load bus in Lehigh.dss | Load Description | LoadShape column in lehigh_load.csv | Questions | Max Load (kW) as per bus loads defined in IEEE13 | Average Load (kW) | Max Load (kW) | Min Load (kW) | $/kWh | $/kw/month | Generation Mix: | Length of Outage (hr specified): | Start hour of outage | Recommended Diesel (kW) | Recommended Solar (kW) | Recommended Battery Power (kW) | Recommended Battery Capacity (kWh) | Rough upfront cost ($) | Res NPV ($) | CapEx | CapEx after incentives | Res Average outage survived (hr): | Res Prob surviving 48 hr outage (%) | Result:
m1 | '634a','634b','634c' | '632633' | 634 |  |  |  | 400 | 178 | 306 | 60 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 196 | 400 | 39 | 106 | 815280 | -48637 | 814580 | 508910 | 84
m1 | 634a |  |  | 24-hour operations | 634a_supermarket |  | 160
m1 | 634b |  |  | 24-hour operations | 634b_supermarket |  | 120
m1 | 634c |  |  | 24-hour operations | 634c_supermarket |  | 120
m2 | '675a','675b','675c' | 671692' | '675' |  |  |  | 772.9 | 163 | 389 | 53 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 134 | 324 | 43 | 106 | 666040 | 10462 | 666568 | 414147 | 23 |  | Resilience is much lower than expected: I don't think the Lehigh_reopt/Loadshape.csv is being built correctly, as the loads are way less than the sum of the loads specified in the microgrid
m2 | 675a |  |  | Residential Building | 675a_hospital |  | 485
m2 | 675b |  |  | Residential Building | 675b_residential1 | 652_med_apartment Is the basis | 68
m2 | 675c |  |  | Residential Building | 675c_residential1 |  | 290
m3 | '611','652' | '671684' | 684 |  |  |  | 298 | 145 | 270 | 60 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 155 | 11 | 20 | 62 | 137940 | -95326 | 137677 | 119617 | 14
m3 | 611 |  |  | Tower | 611_hotel |  | 170
m3 | 652 |  |  | Residential Building | 652_med_apartment |  | 128
m4 | '645','646' | 632645 | 646 |  |  |  | 363 | 139 | 384 | 25 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 132 | 312 | 57 | 134 | 669360 | -37742 | 670106 | 420744 | 23
m4 | 645 |  |  | Hangar | 645_warehouse1 |  | 170
m4 | 646 |  |  | Operations Center | 646_med_office |  | 230
TOTALS FOR 4 ISOLATED MICROGRIDS | [7 empty] | 625 | 1349 | 198 |  |  |  |  | Totals for 4-isolated microgrids: | 617 | 1047 | 159 | 408 | 2288620 | -171243 | 2288931 | 1463418 | 36
Full grid | 634a_supermarket','634b_supermarket','634c_supermarket','675a_residential1','675b_residential1','675c_residential1','611_hotel','652_med_apartment','645_warehouse1','646_med_office' | 650632' | 670 | Critical loads? All loads in above microgrids, but not the other buses to make the full load of the base |  |  |  | 626 | 1311 | 266 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 570 | 1378 | 230 | 560 | 2918200 | -72114 | 2918280 | 1825515 | 44
DIFFERENCES | [7 empty] | -1 | 38 | -68 |  |  |  |  | Differences between isolated and grouped grid: | 47 | -331 | -71 | -152 | -629580 | -99129 | -629349 | -362097 |  |  | Similar result in everything but solar, in which the full scale grid needs an additional 300 kW, making it $360k more expensive upfront, but $100k better (less negative) NPV

## 12222020_Lehigh
Lehigh.dss 4 microgrid system | [17 empty] | 240 | 168
480
Json converter: https://onlinejsontools.com/convert-json-to-text
Reopt API docs: https://developer.nrel.gov/docs/energy-optimization/reopt-v1/
[16 empty] | Scenario constants: | Miami, FL; outage; critical load factor 70%; 2017; 30,000 gallons of diesel (not all of which gets burned)
[10 empty] | *To build the demand_loads for each microgrid, I ran the full model in microgrid.py and pulled the loadshapes from loadShape.csv |  | 0.40181
[10 empty] | *Calculated using all loads connected to gen bus added together | [5 empty] | *Resilience optimization outputs |  |  |  | *without incentives | *I am not sure that the NPV includes capital cost? |  |  | *minimum survived outage is often 0 hours
Microgrid name | Loads in Lehigh.dss | Switch in Lehigh.dss | load bus in Lehigh.dss | Load Description | LoadShape column in lehigh_load.csv | Questions | Max Load (kW) as per bus loads defined in IEEE13 | Average Load (kW) as of 12/22/2020 | Max Load (kW) as of 12/22/2020 | Min Load (kW) as of 12/22/2020 | $/kWh | $/kw/month | Generation Mix: | Length of Outage (hr specified): | Start hour of outage | Recommended Diesel (kW) | Recommended Solar (kW) | Recommended Battery Power (kW) | Recommended Battery Capacity (kWh) | Rough upfront cost ($) | Res NPV ($) | CapEx | CapEx after incentives | Res Average outage survived (hr): | Res Prob surviving 48 hr outage (%) | Result:
m1 | '634a','634b','634c' | '632633' | 634 |  |  |  | 400 | 178 | 306 | 60 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 196 | 400 | 39 | 106 | 815280 | -48637 | 814580 | 508910 | 84
m1 | 634a |  |  | 24-hour operations | 634a_supermarket |  | 160
m1 | 634b |  |  | 24-hour operations | 634b_supermarket |  | 120
m1 | 634c |  |  | 24-hour operations | 634c_supermarket |  | 120
m2 | '675a','675b','675c' | 671692' | '675' |  |  |  | 772.9 | 430 | 700 | 111 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 134 | 324 | 43 | 106 | 666040 | 10462 | 666568 | 414147 | 23 |  | Resilience is much lower than expected: I don't think the Lehigh_reopt/Loadshape.csv is being built correctly, as the loads are way less than the sum of the loads specified in the microgrid
m2 | 675a |  |  | Residential Building | 675a_hospital |  | 485
m2 | 675b |  |  | Residential Building | 675b_residential1 | 652_med_apartment Is the basis | 68
m2 | 675c |  |  | Residential Building | 675c_residential1 |  | 290
m3 | '611','652' | '671684' | 684 |  |  |  | 298 | 145 | 270 | 60 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 155 | 11 | 20 | 62 | 137940 | -95326 | 137677 | 119617 | 14
m3 | 611 |  |  | Tower | 611_hotel |  | 170
m3 | 652 |  |  | Residential Building | 652_med_apartment |  | 128
m4 | '645','646' | 632645 | 646 |  |  |  | 363 | 139 | 384 | 25 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 132 | 312 | 57 | 134 | 669360 | -37742 | 670106 | 420744 | 23
m4 | 645 |  |  | Hangar | 645_warehouse1 |  | 170
m4 | 646 |  |  | Operations Center | 646_med_office |  | 230
TOTALS FOR 4 ISOLATED MICROGRIDS | [7 empty] | 892 | 1660 | 256 |  |  |  |  | Totals for 4-isolated microgrids: | 617 | 1047 | 159 | 408 | 2288620 | -171243 | 2288931 | 1463418 | 36
Full grid | 634a_supermarket','634b_supermarket','634c_supermarket','675a_residential1','675b_residential1','675c_residential1','611_hotel','652_med_apartment','645_warehouse1','646_med_office' | 650632' | 670 | Critical loads? All loads in above microgrids, but not the other buses to make the full load of the base |  |  |  | 626 | 1311 | 266 | 0.08 | 20 | PV + Battery + Diesel | 168 | 240 | 570 | 1378 | 230 | 560 | 2918200 | -72114 | 2918280 | 1825515 | 38
DIFFERENCES | [7 empty] | 266 | 349 | -10 |  |  |  |  | Differences between isolated and grouped grid: | 47 | -331 | -71 | -152 | -629580 | -99129 | -629349 | -362097 |  |  | Similar result in everything but solar, in which the full scale grid needs an additional 300 kW, making it $360k more expensive upfront, but $100k better (less negative) NPV

## 121620_Lehigh
Lehigh.dss 4 microgrid system
solar_mult_2017.csv was based on the REopt financial analysis output (with no specified outages!) of a 400 kW pv system putting out on average 650,000 kWH per year in Texas in 2017. The loadshape is scaled to reflect this total production, producing up to 75% of total kVA of the solar panels at one time. | [17 empty] | Json converter: https://onlinejsontools.com/convert-json-to-text
battery_mult_2017.csv was based on the output of a 31.3 kWH, 11.9 kW battery system putting out about 6440 kWH per year in Texas in 2017. The loadshape is scaled to reflect this total production, producing up to 100% of total kW output in one hour. | [17 empty] | Reopt API docs: https://developer.nrel.gov/docs/energy-optimization/reopt-v1/
diesel_mult_2017.csv was based on the output of a 107 kVA diesel generato in Texas in 2017. The loadshape is scaled to reflect high utility rate production using diesel to shave peak demand during the summer months mostly, producing up to 100% of total kW output in one hour.
Solar_mult_2017, battery_mult_2017 and diesel_mult_2017 work together within the same microgrid to balance eachother's load | [15 empty] | Scenario constants: | Miami, FL; outage; critical load factor 70%; 2017; 30,000 gallons of diesel (not all of which gets burned)
[10 empty] | *To build the demand_loads for each microgrid, I used the associated csv column, adjusted to the max load, and added the shapes together, loading it into the save "1606" run from Reopt web tool on 11/19/2020 |  | 0.40181
[10 empty] | *Calculated using all loads connected to gen bus added together | [5 empty] | *Resilience optimization outputs |  |  |  | *without incentives | *I am not sure that the NPV includes capital cost? | *minimum survived outage is often 0 hours
Microgrid name | Loads in Lehigh.dss | Switch in Lehigh.dss | load bus in Lehigh.dss | Load Description | LoadShape column in lehigh_load.csv | Questions | Max Load (kW) as per bus loads defined in IEEE13 | Average Load (kW) as of 12/17/2020 | Max Load (kW) as of 12/17/2020 | Min Load (kW) as of 12/17/2020 | $/kWh | $/kw/month | Generation Mix: | Length of Outage (hr specified): | Start date of outage | Recommended Diesel (kW) | Recommended Solar (kW) | Recommended Battery Power (kW) | Recommended Battery Capacity (kWh) | Rough upfront cost ($) | Res NPV ($) | Res Average outage survived (hr): | Res Prob surviving 168 hr outage (%) | Result:
m1 | '634a','634b','634c' | '632633' | 634 |  |  |  | 400 | 194 | 334 | 65 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 165 | 440 | 79 | 307 | 981800 | -1521 | 2024 | 77
m1 | 634a |  |  | 24-hour operations | 634a_supermarket |  | 160
m1 | 634b |  |  | 24-hour operations | 634b_supermarket |  | 120
m1 | 634c |  |  | 24-hour operations | 634c_supermarket |  | 120
m2 | '675a','675b','675c' | 671692' | '675' |  |  | Should load at 692 be served by m2? | 772.9 | 312 | 700 | 111 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 265 | 1234 | 198 | 553 | 2505480 | 214920 | 307 | 54
m2 | 675a |  |  | Residential Building | 675a_residential1 |  | 485
m2 | 675b |  |  | Residential Building | 675b_residential1 | What is the basis of this load shape? | 68
m2 | 675c |  |  | Residential Building | 675c_residential1 |  | 290
m3 | '611','652' | '671684' | 684 |  |  |  | 298 | 275 | 500 | 114 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 81 | 432 | 83 | 225 | 895920 | 109888 | 1067 | 87
m3 | 611 |  |  | Tower | 611_hotel | *671 was reworked as 611 to match the outline of the model | 170 | 200 | 351 | 85
m3 | 652 |  |  | Residential Building | 652_med_apartment |  | 128
m4 | '645','646' | 632645 | 646 |  |  |  | 363 | 150 | 412 | 26 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 145 | 590 | 98 | 346 | 1244140 | 20343 | 216 | 41
m4 | 645 |  |  | Hangar | 645_warehouse1 |  | 170
m4 | 646 |  |  | Operations Center | 646_med_office |  | 230

## 112320_Lehigh.dss
Lehigh.dss 4 microgrid system
solar_mult_2017.csv was based on the REopt financial analysis output (with no specified outages!) of a 400 kW pv system putting out on average 650,000 kWH per year in Texas in 2017. The loadshape is scaled to reflect this total production, producing up to 75% of total kVA of the solar panels at one time. | [15 empty] | Json converter: https://onlinejsontools.com/convert-json-to-text
battery_mult_2017.csv was based on the output of a 31.3 kWH, 11.9 kW battery system putting out about 6440 kWH per year in Texas in 2017. The loadshape is scaled to reflect this total production, producing up to 100% of total kW output in one hour. | [15 empty] | Reopt API docs: https://developer.nrel.gov/docs/energy-optimization/reopt-v1/
diesel_mult_2017.csv was based on the output of a 107 kVA diesel generato in Texas in 2017. The loadshape is scaled to reflect high utility rate production using diesel to shave peak demand during the summer months mostly, producing up to 100% of total kW output in one hour.
Solar_mult_2017, battery_mult_2017 and diesel_mult_2017 work together within the same microgrid to balance eachother's load | [13 empty] | Scenario constants: | Miami, FL; outage; critical load factor 70%; 2017; 30,000 gallons of diesel (not all of which gets burned)
[8 empty] | *To build the demand_loads for each microgrid, I used the associated csv column, adjusted to the max load, and added the shapes together, loading it into the save "1606" run from Reopt web tool on 11/19/2020 |  | 0.40181
[8 empty] | *Calculated using all loads connected to gen bus added together | [5 empty] | *Resilience optimization outputs |  |  |  | *without incentives | *I am not sure that the NPV includes capital cost? | *minimum survived outage is often 0 hours
Microgrid name | Loads in Lehigh.dss | Switch in Lehigh.dss | load bus in Lehigh.dss | Load Description | LoadShape file | Max Load (kW) | Average Load (kW) | Min Load (kW) | $/kWh | $/kw/month | Generation Mix: | Length of Outage (hr specified): | Start date of outage | Recommended Diesel (kW) | Recommended Solar (kW) | Recommended Battery Power (kW) | Recommended Battery Capacity (kWh) | Rough upfront cost ($) | Res NPV ($) | Res Average outage survived (hr): | Res Prob surviving 168 hr outage (%) | Result:
m1 | '634a','634b','634c' | '632633' | 634 |  | 400kW_resid.txt | 400 | 178.38 | 63.57 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 165 | 440 | 79 | 307 | 981800 | -1521 | 2024 | 77
m1 | 634a |  |  | Residential | 400kW_resid.txt | 160
m1 | 634b |  |  | Residential | 400kW_resid.txt | 120
m1 | 634c |  |  | Residential | 400kW_resid.txt | 120
m2 | '675a','675b','675c' | 671692' | '675' |  | m2_load.csv | 772.9 | 426 | 217 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 265 | 1234 | 198 | 553 | 2505480 | 214920 | 307 | 54
m2 | 675a |  |  | hospital | hospital.txt | 485
m2 | 675b |  |  | Data Center | supermarket.txt | 68
m2 | 675c |  |  | Office | medium_office.txt | 290
m3 | '611','652' | '671684' | 684 |  | m3_load.csv | 298 | 127.7 | 53.33 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 81 | 432 | 83 | 225 | 895920 | 109888 | 1067 | 87
m3 | 611 |  |  | Hangar | warehouse.txt | 170
m3 | 652 |  |  | Data Center | supermarket.txt | 128
m4 | '645','646' | 632645 | 646 |  | m4_load.csv | 363 | 231 | 89 | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 145 | 590 | 98 | 346 | 1244140 | 20343 | 216 | 41
m4 | 645 |  |  | Tower | hotel_medium.tx | 170
m4 | 646 |  |  | Operations Center | supermarket.txt | 230

## 6_build+resid_11032020
LoadShapes built from https://www.energy.gov/eere/buildings/commercial-reference-buildings using the REopt site: https://reopt.nrel.gov/tool/ with .1 $/kWh and 20$/kW/month demand charge in 2017
Energy.gov reference Loadshapes are not built for 24/7 operation, and have dips on weekends
*Assume average of 50% of target load across the whole year
Building to be modeled | Description | Ref building type | Area (ft^2) of reference building | Specified Geography | max kW load target (for modeling Laughlin) | Inputted Annual Consumption (kWh) into Reopt | Average Load (kW) from downloaded shape | Min Load (kW) from downloaded shape | Max Load (kW) from downloaded shape | Default Annual Consumption (kWh, as reported by REopt)
hangar_large_2_e.gov.csv | Large airplane hangar | Warehouse | 52000 | Miami, FL | 300 | 1314000 | 150 | 27.4 | 480 | 202082
hangar_medium_2_e.gov.csv | Medium Airplane hangar | Warehouse | 52000 | Atlanta, GA | 200 | 876000 | 100 | 16.57 | 351.89 | 223009
hospital_e.gov.csv | On-basehospital | Hospital | 241351 | Atlanta, GA | 1000 | 4380000 | 500 | 296 | 801 | 9054747
comms_data_2_e.gov.csv | Communications/office/data center | Medium Office | 53628 | Miami, FL | 600 | 2628000 | 300 | 52.24 | 757.76 | 1021224
terminal_2_e.gov.csv | Terminal building to hoouse recruits | Supermarket | 45000 | Miami, FL | 500 | 2190000 | 250 | 83.87 | 429.38 | 2260929
tower_e.gov.csv | Flight tower with radar, etc | Hotel Small | 5500 | Miami, FL | 400 | 1752000 | 200 | 85 | 351 | 972090
3MW_resid_e.gov.csv | Residential load | Midrise Apartment | 33740 | Miami, FL | 3000 | 13140000 | 1500 | 535 | 3364 | 424956
6_building_resid_combined_11032020.csv | Full installation load added together |  |  |  |  | 26280000 | 3000 | 1325.5 | 6264
Crit_loads_no_resid_11032020.csv | Critical loads without residual |  |  |  |  | 13140000 | 1500 | 772.3 | 2975
Scenario constants: | Miami, FL; outage; critical load factor 70%; 2017; 20,000 gallons of diesel (not all of which gets burned)
Scenario | LoadShape file | $/kWh | $/kw/month | Generation Mix: | Length of Outage (hr specified): | Start date of outage | Resilience results: | Rough upfront cost | Res NPV ($) | Res Average outage survived (hr): | Res Prob surviving 168 hr outage (%) | Result:
BASE CASE: full load 1 week outage mid summer | 6_building_resid_combined_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 2,214 kW Diesel 8,002 kW PV 1,212 kW Battery 4,055 kWh Battery |  | 1645427 | 292 | 77 | BASE CASE: With unlimited fuel and 70% critical load, system is profitable
full load 1 day outage | 6_building_resid_combined_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 24 | 8/14/2017 8am | 2,181 kW Diesel 7,927 kW PV 1,208 kW Battery 4,010 kWh Battery |  | 2294249 | 281 | 74 | At 24 hour outage with same as base case, system stays largely the same but is more profitable
full load 1 week outage mid winter | 6_building_resid_combined_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 1/16/2017 8am | 1,792 kW Diesel 7,668 kW PV 1,112 kW Battery 3,223 kWh Battery |  | 2180251 | 117 | 27 | Winter resiliency estimate greatly decreases estimate of week-long survivability
Critical (flight ready) loads | Crit_loads_no_resid_11032020.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 976 kW Diesel 4,473 kW PV 673 kW Battery 1,961 kWh Battery |  | 937421 | 393 | 71 | More cost effective (by $700,000) on the larger grid than separating critical and non critical loads, with fewer resources (200kw less genset and 500 kWh less battery) needed in the full mircogrid.
Residential (non-critical) loads | 3MW_resid_e.gov.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 1,387 kW Diesel 3,701 kW PV 660 kW Battery 2,580 kWh Battery |  | -12437 | 544 | 77 | Residential on it's own
Hospital islanded | hospital_egov.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 312 kW Diesel 1,273 kW PV 181 kW Battery 564 kWh Battery |  | 185930 | 316 | 58 | Largest individual load receives more average resiliency, but lower probably of lasting 1 week; is cost effective on it's own
Tower Islanded | tower_egov.csv | 0.1 | 20 | PV + Battery + Diesel | 168 | 8/14/2017 8am | 142 kW Diesel 441 kW PV 95 kW Battery 371 kWh Battery |  | -25266 | 283 | 50 | Smallest individual load is not cost effective to island

## 6_buildings_10282020
33740 | 33.74 | 35 units
19
2009 seattle ecotope data from https://www.seattle.gov/Documents/Departments/OSE/MF-Billing-Analysis-MidRise2009.pdf
at ~70% energy from electricity
Units | kWh/yr | kWh/yr/unit
19 | 184036 | 9686.1053
49 | 297959 | 6080.7959
44 | 427938 | 9725.8636
mean |  | kWh/yr/unit |  |  |  | kWhr/day/unit
76 | 505713 | 6654.1184 |  |  |  | 18.2305
|  | 232894.1447 |  | Average annual consumtion kWh for a 35 unit building of 1000 square ft units in Seattle
LoadShapes built from https://www.energy.gov/eere/buildings/commercial-reference-buildings using the REopt site: https://reopt.nrel.gov/tool/ with .1 $/kWh and 20$/kW/month demand charge in 2017
Energy.gov reference Loadshpaes are not built for 24/7 operation, and have dips on weekends
*Assume average of 50% of target load across the whole year
Building to be modeled | Description | Ref building type | Area (ft^2) of reference building | Specified Geography |  | max kW load target (for modeling Laughlin) | Inputted Annual Consumption (kWh) into Reopt | Average Load (kW) from downloaded shape | Min Load (kW) from downloaded shape | Max Load (kW) from downloaded shape | Default Annual Consumption (kWh, as reported by REopt) |  | 10000
hangar_large_e.gov.csv | Large airplane hangar | Warehouse | 52000 | Miami, FL |  | 1000 | 4380000 | 500 | 91.5 | 1599 | 202082 | *refit with residential | 6
hangar_medium_e.gov.csv |  | Warehouse | 52000 | Atlanta, GA |  | 800 | 3504000 | 400 | 66.27 | 1408 | 223009 | *refit with residential
hospital_e.gov.csv | On-basehospital | Hospital | 241351 | Atlanta, GA |  | 1000 | 4380000 | 500 | 296 | 801 | 9054747
comms_data_e.gov.csv | Communications/office/data center | Medium Office | 53628 | Miami, FL |  | 1000 | 4380000 | 500 | 87 | 1263 | 1021224
terminal_e.gov.csv | Terminal building to hoouse recruits | Supermarket | 45000 | Miami, FL |  | 800 | 3504000 | 400 | 134 | 687 | 2260929
tower_e.gov.csv | Flight tower with radar, etc | Hotel Small | 5500 | Miami, FL |  | 400 | 1752000 | 200 | 85 | 351 | 972090
|  |  |  | Sum: |  | 5000 | 21900000 | 5000 | 1818.77 | 11944 | 13734081
6_building_combined_10282020.csv | Full installation load added together | [5 empty] | 21900002 | 2500 | 1059 | 5835
Analysis of full load 6_building_combined_10282020.csv as prepared by https://reopt.nrel.gov/tool/:
Scenario constants: | .10$/kWh, 10$/kw/month in Miami, FL; outage; critical load factor 70%; loadshape = 6_building_combined_10282020.csv in 2017
*Reopt assumes full battery charge when modeling outage
Generation Mix: | Length of Outage (hr specified): | Start date of outage | Resilience results: | Res NPV | Res Average outage survived: | Res Prob surviving specified outage | Financial results: | Fin NPV | Fin Average outage survived:
PV + Battery | 24 | Jul 25th 2am (peak season | 9,714 kW PV 2,036 kW Battery 13,137 kWh Battery | -1689564 | 8 |  | 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1
PV + Battery+ Wind | 24 | Jul 25th 2am (peak season | Wind not recommended, defaults to PV+Battery as above
PV + Battery + Diesel | 24 | Jul 25th 2am (peak season | 593 kW Diesel 8,653 kW PV 1,551 kW Battery 6,932 kWh Battery | -154734 | 14 |  | 0 kW Diesel 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1
PV + Battery | 168 | Jul 25th 2am (peak season | 11,924 kW PV 2,857 kW Battery 24,388 kWh Battery | -5944586 | 70 | 13% | 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1
PV + Battery+ Wind | 168 | Jul 25th 2am (peak season | 11,638 kW PV 2,810 kW Battery 24,338 kWh Battery 268 kWh Wind | -5920757 | 81 | 16% | 6,284 kW PV 140 kW Battery 185 kWh Battery 14 kWh Wind | 1931723 | 1
PV + Battery + Diesel | 168 | Jul 25th 2am (peak season | 1,666 kW Diesel 6,710 kW PV 368 kW Battery 562 kWh Battery | 357608 | 69 | 12% | 0 kW Diesel 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1 | *Added 15000 gallons of diesel available to get this to turn on
PV + Battery + Diesel | 168 | Feb 2 2am (offpeak season) | 1,920 kW Diesel 6,705 kW PV 731 kW Battery 1,449 kWh Battery | 67193 | 164 | 59%
PV + Battery + Diesel | 168 | July 3 4pm (annual peak auto selected) | 1,823 kW Diesel 6,857 kW PV 756 kW Battery 1,263 kWh Battery | 116395 | 158 | 55% |  |  |  | *Reopt assumes 13.16 kWh per gallon of diesel, which is a little low for a 1MW genset
PV + Battery | N/A on microgridDesign | [5 empty] | 0 kW Diesel 6,286 kW PV 138 kW Battery 182 kWh Battery | 1931671 | 1 | *not incorporating the resiliency outputs based on outages in microgridDesign, and the economic is not what we need