## Sheet1
Goal: to figure out the JSON needed to trigger an outage, "resiliency run" and generator optmization.
Set inputs:Generator with standard utility rates format matching microgridDesign and custom LoadProfile; utility rates and loadProfile pulled from Scenario _test_POST.json
default=660 gallons
File tested | Inputs |  |  |  |  | PV | Storage | Storage | Wind | Wind | Generator | Generator | Generator | Generator | Generator | Generator | Generator | Outputs | run_uuid | Outcome Notes | PV | Storage | Storage | Wind | Generator | Generator |  | Outputs | resultsResilience_S12.json
| critical_load_pct | outage_start_hour | outage_end_hour | blended_annual_rates_us_dollars_per_kwh | blended_annual_demand_charges_us_dollars_per_kw | max_kw | max_kw | max_kwh | max_kw | installed_cost_us_dollars_per_kw | "fuel_avail_gal" | existing_kw | min_kw | max_kw | generator_only_runs_during_grid_outage | generator_sells_energy_back_to_grid | min_turn_down_pct | results_S11.json |  |  | "size_kw" | "size_kw" | "size_kwh" | "size_kw" | fuel_used_gal | "size_kw" | npv_us_dollars | resultsResilience_S12.json | avg_critical_load
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 |  | 1000 | 0 | 0 | 500 | FALSE | FALSE | Empty | Null | 653ee116-05d2-4ce9-b0ca-b3ae93a0081c | Timed out and returned null result after 420 seconds | [7 empty] | Null
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 |  | 1000 | 0 | 0 | 500 | FALSE | FALSE | Empty | Pass |  | Specific generator settings can be set when no battery is specified | 277 | 0 | 0 | 0 | 1000 | 105.166 |  | Pass
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 |  | 1000 | 0 | 0 | 0 | FALSE | FALSE | Empty | Null | Status code 500 error | The logic around specifying generator attributes comes into conflict when battery is also included in the mix
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 | Empty | 1000 | 0 | 0 | 0 | TRUE | FALSE | Empty | Null | Status code 500 error
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 | Empty | 1000 | 0 | 0 | 0 | FALSE | TRUE | Empty | Null | Status code 500 error
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Pass |  | When outage is inputted and nothing is filled in for generator, then defaults are used for generator and generator is automatically optimized for | 320 | 47 | 155 | 0 | 61 | 57.8 |  | Pass | 68.2
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 | Empty | Empty | Empty | Empty | 0 | Empty | Empty | Empty | Null | Status code 500 error | Can't force generator off by setting max_kw to 0 when an outage is specified
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Pass |  |  | 264 | 0 | 0 | 0 | 72.6 | 105 | 58148 | Pass | 68.2055
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | Empty | 40 | Empty | Empty | Empty | Empty | Empty | Pass |  | Inputting existing generator changes NPV but does not change optimal total gen "size_kw" | 264 | 0 | 0 | 0 | 72.6 | 105 | 82058 | Pass
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 1000 | default=11950 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Pass |  |  | 264 | 0 | 0 | 0 | 72.6 | 105 |  | Pass
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 1000 | 500 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Pass |  | Need to lower the price per kw of Wind below default to make it trigger | 260.8 | 0 | 0 | 52.1 | 57 | 99 | 63242 | Pass | 68.2055
Scenario_POST11.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 0 | 100 | 500 | 0 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Pass |  |  | 0 | 4.28 | 12.4 | 0 | 139.4 | 113.4 | -71184 | Pass
Scenario_POST11.json | 0.5 | 1000 | 1024 | 0.12 | 20 | 0 | 100 | 500 | 0 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Empty | Pass |  | runResilience() seems to running correctly in Reopt/__init__.py; avg_critical_load changes mainly based on targeted critical load | 0 | 3.76 | 12 | 0 | 99.5 | 80 | -50261 | Pass | 48.7182
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | 1000 | 0 | 0 | 500 | FALSE | FALSE | Empty | Pass |  | Did I change the location on otherwise identical run from POST11 in Row 7? | 262 | 0 | 0 | 0 | 1000 | 97.3 | 170083 | Pass | 68.2055
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | 1000 | 0 | 0 | 500 | FALSE | FALSE | 0.3 | Null | Status code 500 error | Inputting min_turn_down_pct in conjunction with specifying other generator properties is not recommended | [7 empty] | Fail
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | Empty | Empty | Empty | Empty | Empty | Empty | 0.3 | Pass | fb2c382f-bd84-4112-a6af-f575a7a8d16b | Setting min_turn_down_pct does not change size of generator, just makes it run much less often, altering size_kw of PV slightly, but changing NPV a lot; Rec: Set min_turn_down_pct to 0.3 as recommended by Caterpillar for large gensets over 1/2 hour timescales | 258.5 | 0 | 0 | 0 | 90.3 | 97.3 | 79323 | Pass | 68.2055
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | 30000 | Empty | Empty | Empty | Empty | Empty | 0.3 | Pass |  | Setting "fuel_avail_gal" above default=660 is necessary, but it seems to break the resilience results if too high; | 258.5 | 0 | 0 | 0 | 90.3 | 97.3 | 79323 | Fail
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | 10000 | Empty | Empty | Empty | Empty | Empty | 0.3 | Pass |  |  | 258.5 | 0 | 0 | 0 | 90.3 | 97.3 | 79323 | Fail
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 0 | 0 | 0 | Empty | 1000 | Empty | Empty | Empty | Empty | Empty | 0.3 | Pass |  | Need to allow runResilience to poll for longer with higher "fuel_avail_gal" so it does not fail | 258.5 | 0 | 0 | 0 | 90.3 | 97.3 | 79323 | Pass
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 | Empty | 1000 | Empty | Empty | Empty | Empty | Empty | 0.3 | Pass |  |  | 309 | 46 | 180 | 0 | 66 | 54 | 122609 | Pass
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 0 | Empty | 1000 | 20 | Empty | Empty | Empty | Empty | 0.3 | Pass |  | existing_gen works with battery when only 3 generator parameters are set; gen "size_kw" = existing + additional diesel generation | 309 | 46 | 180 | 0 | 66 | 54 | 134564 | Pass
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 500 | Empty | 1000 | 20 | Empty | Empty | Empty | Empty | 0.3 | Pass |  | Wind does not trip the optimization, but times out the resiience run | 309 | 46 | 180 | 0 | 66 | 54 | 134564 | Fail
Scenario_POST13.json | 0.7 | 1000 | 1024 | 0.12 | 20 | 500 | 100 | 500 | 500 | 100 | 1000 | 20 | Empty | Empty | Empty | Empty | 0.3 | Pass |  | I think this is all of the inputs we want, with wind triggered and working | 301 | 44 | 170 | 56 | 67 | 55 | 138725 | Pass